TIER I ES&H INSPECTION GUIDE FOR FACILITY INSPECTIONS

Fire Safety Tier I Inspection Checklist

| Inspection Team Members: |
| --- |
| Location: | Date: |

| A. HOUSEKEEPING AND WORKPLACE/STORAGE |
| --- |
| 1. | ( | Remove unnecessary accumulations of combustible materials from the workplace. (Ref: Fire Safety S.A. 3.1 (6) & NYS FC 305.1) |
| 2. | ( | Combustible materials stored at least 36 inches away from potential ignition sources such as electric baseboard heat, gas- and oil-fired hot water heaters, furnaces, etc. (Ref: Fire Safety S.A. & NYS FC 315.2) |
| 3. | ( | Minimum clearance distances (noted on labels attached to heating and cooking devices) are followed. (Ref: Fire Safety S.A. 3.2) |
| 4. | ( | Boiler rooms, mechanical rooms and electrical equipment rooms are free of combustible storage. (Ref.: NYS FC 315.2.3) |
| 5. | ( | Clearance between the ceiling and storage is at least 2 feet in non-sprinklered buildings or at least 18 inches below sprinkler heads in sprinklered buildings. (Ref: Fire Safety S.A. & NYS FC 315.2.1) |
| 6. | ( | Combustibles stored outdoors are not stored beneath combustible unsprinklered overhangs, under non-sprinklered eaves, or canopies or other projections. (Ref: NYS FC 315.3.1) |
| B. SPACE HEATERS (Ref. Fire Safety S.A. 1.1) |
| 1. | ( | BNL approval label displayed on the space heaters. |
| 2. | ( | Building and room on label corresponds to location of space heater. |
| 3. | ( | User of the space heater trained in safe use of the space heater. |
| 4. | ( | Combustibles at least 3 feet away from the heater. |
| C. HOT WORK AND IGNITION SOURCES (Ref: Fire Safety S.A. 2.1) |
| 1. | ( | Hot Work has been assessed and approved in accordance with the BNL Fire Safety Subject Area, Section 2.1. |
| 2. | ( | Have hot work permit. |
| 3. | ( | Ornamental, decorative or scented candles are not in use. Incense is not in use. |
| D. EMERGENCY LIGHTS (Ref: Fire Safety S.A. & NYS FC) |
| 1. | ( | Emergency lights are provided and functional for hallways and exit paths in offices (only offices with night shifts), in all laboratory occupancies, or industrial occupancies (shop, manufacturing or storage). (Note: Buildings with emergency generators do not require battery lights) |
| E. EXTERIOR |
| 1. | ( | Smoking limited to designated areas. (Ref. Fire Safety S.A. 1.4) |
| 2. | ( | Smoking areas are outdoors and are a minimum of 10 feet away from containers that are used for combustible materials. (Ref. Fire Safety S.A. 1.4) |
| 3. | ( | Smoking areas are a minimum of 25 feet away from flammable liquid/gas storage areas. (Ref. Fire Safety S.A. 1.4) |
| 4. | ( | No accumulation of leaves/debris is by the “butt stops”. |
| 5. | ( | Exterior doors are fully operable and free of obstructions. |
| 6. | ( | Outdoor cooking is accomplished in approved units such as grills, hibachis, and fixed grills. |
| F. FIRE EXTINGUISHERS |
| 1. | ( | Fire extinguishers are charged, unobstructed and un-obscured. (Note: a sign denoting the location is an acceptable alternative to an obscured extinguisher) (Ref: NYS FC 906.6) |
| 2. | ( | Portable fire extinguishers are housed in NRTL cabinets mounted to the wall or installed on hangers or mounted on brackets securely anchored to the wall. (Ref: NYS FC 906.7) |
| G. FIRE DOORS |
| 1. | ( | Fire doors (those marked with BNL Fire Rescue inventory labels) are kept closed or equipped with a functional self-closing device. (Note: Pull the door off the magnet and see if the door swings closed) |
| H. INDUSTRIAL OCCUPANCIES |
| 1. | ( | Combustible metal turnings and/or chips are removed daily (Ref: Fire Safety S.A.) |
| 2. 3. | ( ( | Battery Charging Area: Ventilation must be maintained to prevent dangerous accumulation of flammable gases (NYS FC 309.3). Combustible storage is at least 3 feet away from battery charging area (NYS FC 309.2) |
| 4. | ( | Oil-soaked rags are kept in metal containers with tight-fitting metal lids separated by a distance of at least 2 feet from other combustible materials and emptied at the end of each shift. (Ref: Fire Safety S.A. 3.1 & NYS FC 305.2) |
| I. FLAMMABLE LIQUIDS |
| 1. | ( | Flammable liquids that are not in use are returned to storage. |
| 2. | ( | Flammable liquids containers the smallest practical for the present use. |
| 3. | ( | Flammables are used away from any potential ignition sources. |
| 4. | ( | Flammable liquids that are transferred from their original containers are properly labeled and are put in NRTL approved flammable liquid safety containers. (Note: You should see the “UL” label.) |
| 5. | ( | Flammable liquids quantities over 25 gallons are stored in NRTL flammable liquids storage cabinets. |
| J. LIFE SAFETY (Ref: Fire Safety S.A. & NYS FC) |
| 1. | ( | Exit Signs visible and illumination is operational. |
| 2. | ( | Corridors unobstructed to width of exit door. (Note: The hallway leading up to the exit door must be clear and unobstructed and be at least as wide as the door.) |
| 3. | ( | Stairwells and corridors (and nearby alcoves) are free of storage/clutter. |
| 4. | ( | Exit door opens 90 degrees and opening force less than 25 pounds. |

# Footnotes

This checklist is not intended to apply to BNL residential occupancies.  NYS FC refers to the New York State Fire Code.